公司名称: 上海热流环境科技有限公司

Company: SHANGHAI THERMO ECOTECH CO LTD

地址: 上海市奉贤区平安四团安泰路660号

Address: Pingan Industrial Zone, Fengxian Distric Shanghai

样品名称:

Report on the submitted sample said to be: used for DEFINITE PURPOSE CONTACTORS (专用接触器)

| SGS编号: SGS Ref. | : SHEC0051027514EC : SHEC0051027514EC |  |
| --- | --- | --- |
| 型号: Style No. | : 单极, 双极, 叁极 : CY1X***AA (1P) , CY2X***AA( 2P), CY3X***C* (3P) |  |
| 收样日期: Sample Received | : 2011-10-12 : October 12, 2011 |  |
| 审核日期: Survey Period | : 2011-10-12 to 2011-10-17 : October 12 to October 17, 2011 |  |
| 审核要求: Test Requested | 根据客户要求将部品测试报告加以合并 To combine the test reports for the submitted sample |  |
| 测试报告: Test Report | 报告号: Report No. | 报告出具日期: Issue date |
|  | SGS SH430234/CHEM | 11/11/2011 |
|  | SGS SH527355/CHEM | 05/17/2011 |
|  | SGS GLHGO050300692CM | 03/15/2011 |
|  | SGS GZSCR050638944/LP | 06/21/2011 |
|  | SGS SH502026/CHEM | 01/17/2011 |
|  | SGS SH551442/CHEM | 08/02/2011 |
|  | SGS SH559210/CHEM | 08/26/2011 |
|  | SGS SH559212/CHEM | 08/26/2011 |
|  | SGS SH559214/CHEM | 08/26/2011 |
|  | SGS SH559213/CHEM | 08/26/2011 |
|  | SGS SH559211/CHEM | 08/26/2011 |
| 结论: Conclusion | 根据客户提供的报告,针对提供的样品,我们对有关部品数据总结如下 Based on the reports submitted by clients , we outline the test data as following |  |

Signed for and on behalf of

SGS-CSTC Chemical Laboratory

______________________

Ella Zhang

Supervisor

Survey Part

| 部品 No.1 Part name No.1 型号: Model: | 触点 CONTACTS 银氧化锡铟AgSnO2In2O3 AgSnO2In2O3 |
| --- | --- |
| 生产商: Vendor: | 上海松发合金材料有限公司 SHANGHAI SONGFA ALLOY MATERIAL CO., LTD. |
| 报告号: Report number | SGS SH430234/CHEM SGS SH430234/CHEM |
| 部品 No.2 Part name No.2 型号: Model: | 酚醛模塑料 PHENOLIE MOULDING COMPOUND PF2A4-161(PF2A4-161J) PF2A4-161(PF2A4-161J) |
| 生产商: Vendor: | 上海双树塑料厂 SHANGHAI TWIN-TREE PLASTIC FACTORY |
| 报告号: Report number | SGS SH527355/CHEM SGS SH527355/CHEM |
| 部品 No.3 Part name No.3 型号: Model: | 塑料 PLASTIC FR283 FR283 |
| 生产商: Vendor: | LIXIN ENGINEERING PLASTICS CO., LTD. LIXIN ENGINEERING PLASTICS CO., LTD. |
| 报告号: Report number | SGS GLHGO050300692CM SGS GLHGO050300692CM |
| 部品 No.4 Part name No.4 型号: Model: | 铁芯 E-LAMINATION / / |
| 生产商: Vendor: | 温州华正铁芯制造有限公司 WENZHOU HUAZHENG IRON CORE PORDUCE CO., LTD. |
| 报告号: Report number | SGS GZSCR050638944/LP SGS GZSCR050638944/LP |
| 部品 No.5 Part name No.5 型号: Model: | 高温胶带 TAPE PB-416C PB-416C |
| 生产商: Vendor: | 群立胶带(莆田)有限公司 群立胶带(莆田)有限公司 |
| 报告号: Report number | SGS SH502026/CHEM SGS SH502026/CHEM |
| 部品 No.6 Part name No.6 型号: Model: | 插片 PINS 0.8/H62Y2 0.8/H62Y2 |
| 生产商: Vendor: | 上海热流环境科技有限公司 SHANGHAI THERMO ECOTECH CO LTD |
| 报告号: Report number | SGS SH551442/CHEM SGS SH551442/CHEM |
| 部品 No.7 Part name No.7 型号: Model: | 安装底板 MOUNTING PLATE A3 A3 |
| 生产商: Vendor: | 上海热流环境科技有限公司 SHANGHAI THERMO ECOTECH CO LTD |
| 报告号: Report number | SGS SH559210/CHEM SGS SH559210/CHEM |
| 部品 No.8 Part name No.8 型号: Model: | 安装螺丝 MOUNTING SCREW A3 A3 |
| 生产商: Vendor: | 上海热流环境科技有限公司 SHANGHAI THERMO ECOTECH CO LTD |
| 报告号: Report number | SGS SH559212/CHEM SGS SH559212/CHEM |
| 部品 No.9 Part name No.9 型号: Model: | 弹簧 SPRING 1CrNi19 1CrNi19 |
| 生产商: Vendor: | 上海热流环境科技有限公司 SHANGHAI THERMO ECOTECH CO LTD |
| 报告号: Report number | SGS SH559214/CHEM SGS SH559214/CHEM |
| 部品 No.10 Part name No.10 型号: Model: | 动静触桥 MOVING/STATIONARY CONTACT BRIDGE H62 H62 |
| 生产商: Vendor: | 上海热流环境科技有限公司 SHANGHAI THERMO ECOTECH CO LTD |
| 报告号: Report number | SGS SH559213/CHEM SGS SH559213/CHEM |
| 部品 No.11 Part name No.11 型号: Model: | 磁线 MAGNETIC WIRE ZUEW/155 ZUEW/155 |
| 生产商: Vendor: | 上海热流环境科技有限公司 SHANGHAI THERMO ECOTECH CO LTD |
| 报告号: Report number | SGS SH559211/CHEM SGS SH559211/CHEM |

数据总结

Test Data Summary

| Test items |  | Lead (Pb) | Cadmium (Cd) | Mercury (Hg) | Chromium Cr(VI) | PBBs | PBDEs |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Unit |  | ppm | ppm | ppm | ppm | ppm | ppm |
| Detection limit (MDL) in SGS |  | 2 | 2 | 2 | 2 | 5 | 5 |
| Part No.1 | 触点 CONTACTS | N.D. | N.D. | N.D. | N.D. | N.C. | N.C. |
| Part No.2 | 酚醛模塑料 PHENOLIE MOULDING COMPOUND | 11 | N.D. | N.D. | N.D. | N.D. | N.D. |
| Part No.3 | 塑料 PLASTIC | N.D. | N.D. | N.D. | N.D. | N.D. | N.D. |
| Part No.4 | GREY SURFACED METAL | N.D. | N.D. | N.D. | N.D. | N.D. | N.D. |
|  | BLACK SURFACED METAL | N.D. | N.D. | N.D. | N.D. | N.D. | N.D. |
| Part No.5 | 高温胶带 TAPE | 2 | N.D. | N.D. | N.D. | N.D. | N.D. |
| Part No.6 | 插片 PINS | 13 | 4 | N.D. | N.D. | N.C. | N.C. |
| Part No.7 | 安装底板 MOUNTING PLATE | N.D. | N.D. | N.D. | N.D. | N.C. | N.C. |
| Part No.8 | 安装螺丝 MOUNTING SCREW | N.D. | N.D. | N.D. | N.D. | N.C. | N.C. |
| Part No.9 | 弹簧 SPRING | N.D. | N.D. | N.D. | N.D. | N.C. | N.C. |
| Part No.10 | 动静触桥 MOVING/STATIONARY CONTACT BRIDGE | 29 | 6 | N.D. | N.D. | N.C. | N.C. |
| Part No.11 | 磁线 MAGNETIC WIRE | N.D. | N.D. | N.D. | N.D. | N.C. | N.C. |

NOTE:	(1) N.D. = Not detected (<MDL)

(2) N.C. = Not conducted

(3) ppm = mg/kg

Disclaim :

(1) The detection limit of other labs may be different from that of SGS

(2) SGS take no responsibility for any mistakes caused by inaccurate and/or invalid information submitted by the applicant.

*** End of Report ***

Sample photo